## Cover Page
Version 22.3 30/11/22
Add photo
Notes:
This template may require adjustments by individual operators to meet specific reporting requirements as defined in the site Permit(s)
Annual Performance Report 2022
Permit EPR/XP3935TX/V004
Severn Waste Services Limited
EnviRecover
Year: | 2022
Address: | Hartlebury Trading Estate, Hartlebury, Kidderminster DY10 4JD
Tel: | 01905 761680
Email: | enquiries@severnwaste.co.uk
Prepared by: | Sandy Edge | Position: | Environmental Technician
Approved by: | Jasen Jordan | Position: | Plant Manager
Version: | 1
Issue Date: | 20.01.23
Print Report
Print as PDF

## Contents
Annual Performance Report 2022 |  | Severn Waste Services Limited
Contents |  |  |  | Notes:
Section | Subject |  | Page | Section references and Page nos. to be inserted
1 | Facility Information |  | 3 | Sections and Subjects may require adjustment by individual operators to meet specific reporting requirements as defined in the sites Permit(s)
2 | Operational Data |  | 4
3 | Operational Summary |  | 6
4 | Performance Form 1 |  | 7
5 | Energy Form 1 |  | 8
6 | Permit Compliance |  | 9
7 | Improvements |  | 10
8 | Public Liasion |  | 11
9 | Carbon dioxide and nitrous oxide emissions |  | 12
10 | Residue Quality |  | 14
11 | Emissions to Water |  | 15
12 | Emissions to Air (periodically monitored) |  | 16
13 | Emissions to Air (continuously monitored) |  | 17
14 | Hydrogen Chloride emissions |  | 18
15 | Sulphur Dioxdie emsissions |  | 19
16 | Oxides of Notrigen emissions |  | 20
17 | Total Organic Carbon emissions |  | 21
18 | Particulate Matter emissions |  | 22
19 | Carbon Monoxide emissions |  | 23
20 | Ammonia emissions |  | 24
Version Control
Section | Information |  | Date
Distribution
Copy | Name, Role |  | No.
This report is required under the Industrial Emissions Directive’s Article 55(2) requirements on reporting and public information on waste incineration plants and co-incineration plants, which require the operator to produce an annual report on the functioning and monitoring of the plant and make it available to the public.

## Facility Info
Annual Performance Report 2022 | Severn Waste Services Limited
Plant Description and Design |  | Notes:
EnviRecover Energy from Waste facility is situated on the Hartlebury Trading Estate, some 2 km south east of Hartlebury. The main purpose of the facility is to burn non-hazardous municipal, commercial and industrial waste and to recover energy by producing steam. The steam is then used to power a steam turbo generator which produces electricity for export to the grid. Typical hourly electrical export averaged over the year is 17.7MWh. There is also the capability for further heat export to local consumers, although there is currently no local demand for this outlet. The plant is permitted to process 230,000 tonnes per annum during a typical 8,000 hours of operation. |  | Include summary of plant design, design capacity, no. of combustion lines, electrical and heat capacity and any other general information that descibes the facility, its location and purpose
Summary of Operational Processes and Procedures
Incoming waste vehicles drive into the tipping hall and discharge their loads into the waste storage bunker. Overhead crane grabs load the waste into the furnace feed hopper, from where the waste is fed into the furnace in a controlled manner. A moving combustion grate inside the furnace agitates the waste to ensure a complete burn. Pre-heated primary air is injected into the furnace from underneath the combustion grate. This helps to dry out any wet waste and it provides the oxygen for the fire. Secondary air is introduced above the grate for combustion control, and it also ensures complete combustion. As the waste moves down the grate it passes through several combustion zones until it is fully combusted down to ash. Bottom ash from the combustion grate is quenched with water and then conveyed via a metals extraction system to a concrete storage area prior to removal from site. Two auxiliary oil fired burners are located in the combustion chamber. These are used for starting up the process, and will raise the temperature above the minimum temperature of 850°C for 2 seconds in the combustion chamber. This temperature is specified in the Environmental Permit as the minimum temperature at which waste combustion may occur. In normal operation, continuous operation of the auxiliary burners is not required as the waste fire is self-sustaining. The heat from the combustion of waste is captured by a water tube boiler, evaporators and superheaters which raise steam at 60 bar and 415°C to power a turbo generator. An economiser is fitted downstream of the boiler unit to pre-heat the incoming feed water. The furnace is fitted with an aqueous ammonia injection system in order to control the facility’s emissions of NOx to air through selective non-catalytic reduction. A flue gas treatment centre incorporates a reactor with a dry hydrated lime injection system to neutralise acid flue gases. Activated carbon is also injected into the reactor to reduce the concentrations of heavy metals and dioxins in the combustion gases emitted to air. A bag house filter is used to separate out the resulting particulate matter from the cooled and treated gases. Air pollution control residues from the bag house filter are collected continuously and stored in a dedicated silo prior to removal from the site. The facility has a 75 m stack equipped with a Continuous Emission Monitoring System (CEMS) which continuously monitor for particulates, carbon monoxide (CO), sulphur dioxide (SO2), ammonia (NH3), hydrogen chloride (HCl), oxygen (O2), nitrogen oxides (NOx) and volatile organic compounds (VOC). There is no discharge of process liquids to controlled waters. Uncontaminated surface and roof waters are discharged to the surface water drainage system via a series of interceptors, attenuation lagoons and isolation valves. |  | Include summary of key processes and procedures such as (but not limited to); waste reception, control rooms, grate, bed and bolier, energy & heat generation, cooling systems, residue management, emission controls, health and safety systems, maintenance

## Operational Data
Annual Performance Report 2022 |  |  |  | Severn Waste Services Limited
Operational Data | [8 empty] | Notes:
Plant Size | 230000 |  | tonnes pa | 68 | MWth | 22 | MWe |  | * - RDF to include SRF
No. of combustion lines | 1 |  | No. of Turbines: |  | 1 |  |  |  | ** - CHP plants only
2020 updates include; heat in MWh, water in Litres, NCV in MJ/kg
Waste types received | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | %
Household / Local Authority | tonnes | 46495.03 | 44666.8 | 37810.68 | 44404.72 | 173377.23 | 82.47% |  | Availabiity Definition: 'the availability of a line is to be calculated by the number of hours the line reported Continuously Monitored emission levels to the Regulator through the calendar year divided by the total number of hours in that year. The overall plant availability is calculated as the Mean of all lines in the plant. For clarity this includes periods of Other Than Normal Operating Conditions (OTNOC) and abnormal operation.' Rationale: The primary function of an Energy from Waste facility is the disposal of waste. It follows therefore that the availability of a plant is determined by the period of time a facility spends undertaking this activity.
Commercial & Industrial |  | 9917.18 | 9261.7 | 6159.56 | 11518.34 | 36856.78 | 17.53%
Hazardous | [5 empty] | 0 | -
Clinical | [5 empty] | 0 | -
Waste wood (biomass) | [5 empty] | 0 | -
Refuse Derived Fuel * - H'hold/LA | [5 empty] | 0 | -
Refuse Derived Fuel * - C&I | [5 empty] | 0 | -
Other [Please specify] | [5 empty] | 0 | -
Other [Please specify]
Other [Please specify]
Total waste received |  | 56412.21 | 53928.5 | 43970.24 | 55923.06 | 210234.01 | 100%
Rejected Waste | [5 empty] | 0 | -
Unprocessed waste transferred out | [5 empty] | 0 | -
Total waste combusted |  | 57357.7 | 57073.6 | 37358.6 | 60778.5 | 212568.4 | 101.1%
Energy Useage / Export | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | KWh/te
Power Generated | MWh | 44954 | 43560 | 24164 | 38620 | 151298 | 711.7615
Power Exported |  | 39799.825 | 38417.07 | 21259.745 | 33779.13 | 133255.77 | 626.8842
Power Used on site |  | 5154 | 5153 | 3546 | 5263 | 19116 | 89.9287
Power Imported |  | 0 | 9.61 | 642.093 | 422.388 | 1074.091 | 5.0529
Parasitic Load | % | 11.47% | 11.83% | 14.3% | 13.48% | 12.55%
Thermal Energy Produced ** | MWh |  |  |  |  | 0 | -
Thermal Energy Exported ** | [5 empty] | 0 | -
R1 value (if applicable) | [6 empty] | 0.75
Waste Disposal & Recovery | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | % inputs
APC Residues - produced | tonnes | 1569 | 1379 | 962 | 1836 | 5746 | 2.703%
IBA - produced |  | 11256.8 | 11508.7 | 7373.2 | 11568.7 | 41707.4 | 19.62%
Metals recycling |  | 1070.3 | 1019.4 | 463.24 | 1081.1 | 3634.04 | 1.71%
Tiles |  | 0 | 0 | 30.5 | 0 | 30.5 | 0.01435%
Non-conforming waste |  | 0 | 0 | 19.38 | 0 | 19.38 | 0.009117%
Other |  | 0 | 0 | 0 | 0 | 0 | -
Raw Material Usage | Unit | Q1 | Q2 | Q3 | Q4 | Year Total | kg or Ltr /te
Mains Water | ltrs | 8576 | 9439 | 8338 | 9247 | 35600 | 0.16748
Other Water | ltrs | 0 | 0 | 0 | 0 | 0 | -
Ammonia | kgs | 272.45 | 67.61 | 324 | 604.43 | 1268.49 | 0.0059674
Urea | kgs | 0 | 0 | 0 | 0 | 0 | -
Activated Carbon | kgs | 15270 | 15590 | 11280 | 19790 | 61930 | 0.29134
Lime / hydrated lime | kgs | 615930 | 579690 | 408280 | 686840 | 2290740 | 10.7765
Fuel oil | ltrs | 773 | 70694 | 58460 | 4971 | 134898 | 0.63461
Gas | cf | 0 | 0 | 0 | 0 | 0
Other |  | 0 | 0 | 0 | 0 | 0
Summary | Line/Unit | Q1 | Q2 | Q3 | Q4 | Year Total |  | Hrs in year
Availability of waste combustion by line, hrs | 1 | 2158.75 | 2158.3 | 1465.9 | 2200.5 | 7983.45 | 91.14% | 8760
| 2 |  |  |  |  | 0 | n/a
| 3 |  |  |  |  | 0 | n/a
| 4 |  |  |  |  | 0 | n/a
| 5 |  |  |  |  | 0 | n/a
Overall Availability, mean avg. of all lines, hrs | [5 empty] | 7983.45 | 91.14%
Hours of turbine operations, hrs | 1 | 2160 | 2176 | 1224 | 1868.62 | 7428.62 | 84.8%
Hours of turbine operations, hrs | 2 |  |  |  |  | 0 | n/a
Hours of heat / steam export | [5 empty] | 0 | n/a
Net Calorific Value of waste | MJ/kg | 9.66 | 9.7 | 7.86 | 9.12 |  | -
Abnormal Events | qty. | 0 | 0 | 0 | 0 | 0 | no
Abnormal operation | hours | 0 | 0 | 0 | 0 | 0 | 0%
Permit Breaches | qty. |  |  | 1 |  | 1 | yes

## Operational Summary
Annual Performance Report 2022 | Severn Waste Services Limited
Summary of Plant Operations and Maintenance during the reporting year |  | Notes:
The plant processed 212,569 tonnes throughout 2022 The boiler recorded 7976 operational hours in 2022 and the turbo generator was operational for 7425 hours. The remaining hours of the year were allocated to; 1. The scheduled, annual maintenance shutdown to allow for internal inspections, tests and repairs. This included a minor overhaul of the Turbine. 2. A unscheduled shutdown related to a boiler tube failure from 21st August to the 5th September. 3. National Grid de-energised the 66KV network from 6th December to 9th December for tree felling maintenance programme. |  | Include summary of key operational and/or mainteanance activity undertaken in the year, such as any major component upgrades and/or replacements
Summary of Residue Handling for the reporting year
Incinerator Bottom Ash (IBA) produced at EnviRecover is stockpiled at another facility operated by Severn Waste Services. This stockpile is processed by a third party on an annual basis to recover metals and produce aggregate. Air Pollution Control residues (APCr) are collected by road tanker, loaded directly from the APCr silo. The majority of our APCr is processed by OCO Technologies Ltd to produce carbon-negative aggregates suitable for construction purposes. Some APCr was sent to a backup facility, which is an appropriately licenced landfill. |  | Include in here a summary of residue handling regimes and destinations

## Perf. Form 1
2022 | Annual Reporting Performance Form 1
Permit EPR/XP3935TX/V004 |  |  |  |  | Operator: | Severn Waste Services
Facility: | EnviRecover |  |  |  | Form: | Performance 1
Reporting Period from: |  |  | 2022-01-01 |  | to: | 2022-12-31
2022 | Annual Reporting of Waste Disposal and Recovery
Waste Description |  | Disposal Route(s) |  | Disposal Tonnes |  | Recovery Tonnes |  | % / tonne of waste incinerated
1) Hazardous Wastes
APC Residues |  | D1 |  | 781.9 |  | 4964.6 |  | 2.703%
IBA |  |  |  | 0 |  | 0 |  | -
-
-
Total Hazardous Waste |  |  |  | 781.9 |  | 4964.6 |  | 2.703%
2) Non-Hazardous Wastes
IBA |  |  |  | 0 |  | 41707.3 |  | 19.62%
Ferrous Metal |  |  |  | 0 |  | 3584 |  | 1.686%
Process Water |  |  |  | 0 |  | 0 |  | -
-
-
Total Non-Hazardous Waste |  |  |  | 0 |  | 45291.3 |  | 21.31%
TOTAL WASTE |  |  |  | 781.9 |  | 50255.9 |  | 24.01%
Operator’s comments :
2022 | Annual Reporting of Water and Other Raw Material Usage
Raw Material |  |  |  | Usage |  | Unit | Specific Usage |  | Unit
Mains Water |  |  |  | 35600 |  | m3 | 0.16748 |  | m3/te
Total Water |  |  |  | 35600 |  | m3 | 0.16748 |  | m3/te
Urea / Ammonia |  |  |  | 1268.49 |  | kg | 0.0059674 |  | kg/te
Activated Carbon |  |  |  | 61930 |  | kg | 0.29134 |  | kg/te
Lime / hydrated lime / Sodium Bicarb. |  |  |  | 2290740 |  | kg | 10.7765 |  | kg/te
Operator’s comments :
2022 | Annual Reporting of other performance indicators
Parameter |  | Results by Line
|  | A1 | A2 | A3 | A4 | A5 |  | Turbine 1 | Turbine 2
Operating hours for the year, hours |  | 7983 | [5 empty] | 7429
Number of periods of abnormal operation, qty. |  | 0 | [5 empty] | 0
Cumulative hours of abnormal operation for this year, hours |  | 0 | [5 empty] | 0
Operator’s comments :
Signed: | [5 empty] | Date: | 2023-01-23

## Energy Form 1
2022 | Annual Reporting of Energy Usage/Export
Permit EPR/XP3935TX/V004 |  |  | Operator: | Severn Waste Services
Facility: | EnviRecover |  | Form: | Energy 1
Reporting Period from: |  | 2022-01-01 | to: | 2022-12-31
Energy Source |  | Energy Usage | Unit | Specific Useage (KWh/tonne incinerated
Electricity Produced |  | 151298 | MWh | 711.7615
Electricity Imported |  | 1074.091 | MWh | 5.0529
Electricity Exported |  | 133255.77 | MWh | 626.8842
Gas Oil |  | 134898 | tonnes | 0.63461
Steam/hot water exported |  | 0 | GWh | -
Operator’s comments :
Signed: |  |  |  | Date: | 2023-01-23

## Permit Compliance
Annual Performance Report 2022 |  |  | Severn Waste Services Limited
Summary of Permit Compliance
Compliance with permit limits for continuously monitored pollutants
The plant met its emission limits as shown in the table below:
Substance |  | Percentage time compliant during operation |  |  |  | Notes:
|  | Half-hourly limit |  | Daily limit |  | Report to 2 decimal places, i.e. xx.xx% Please provide a brief summary of each notification or non-compliance in the table (rather than just referring to notifications that were sent to the Regulator).
Particulates |  | 100% |  | 100%
Oxides of nitrogen |  | 100% |  | 100%
Sulphur dioxide |  | 100% |  | 100%
Carbon monoxide |  | 99.72 % (95% of 10-min averages) |  | 100%
Total organic carbon |  | 100% |  | 100%
Hydrogen chloride |  | 100% |  | 100%
Hydrogen fluoride |  | 100% |  | 100%
Summary of any notifications or non-compliances under the permit
Date | Summary of notification or non-compliance [including Line/Reference] |  | Reason |  | Measures taken to prevent reoccurrence
2022-07-20 | A1; CO exceedance. 93.06 % of CO 10 min averages below 150 mg/m3 |  | Waste insufficiently mixed. |  | Increased focus on mixing when bunker stocks are high has avoided a reoccurance.
Summary of any complaints received and actions to taken to resolve them.
Date | Summary of complaint [including Line/Reference] |  | Reason * |  | Measures taken to prevent reoccurrence
2022-05-13 | Noise complaint (substantiated by operator) |  | Source identified as steam relief valve. |  | ACC back pressure settings adjusted. Alarm settings adjusted to reflect.
2022-08-21 | High pitched tone and burnt plastic odour. |  | Unsubstantiated - plant off at time of incident.
2022-08-25 | Odour (substantiated by operator) |  | Tipping hall door open / ventilation issue due to extended outage. |  | Extensive maintenance undertaken in 2022 to prevent repeat.
2022-09-06 | Noise complaint (substantiated by operator) |  | Disab units running during outage |  | Future Disab work only to be carried out during working hours.
2022-09-09 | Odour(substantiated by operator) |  | Fault on tipping hall door preventing automatic closing |  | Door monitored / manually closed until fault corrected.
* including whether substantiated by the operator or the EA

## Improvements
Annual Performance Report 2022 | Severn Waste Services Limited
Summary of Plant Improvements
Summary of any efficiency improvements that have been completed within the year.
1. Continual upgrade of refractory within the boiler 1st pass 2. Replacement of all filters within the filter bag house due to end of life cycle 3. Boiler efficiency performance test completed
Summary of any permit improvement conditions that have been completed within the year and the resulting environmental benefits.
None
Summary of any changes to the plant or operating techniques which required a variation to the permit and a summary of the resulting environmental impact.
None
Summary of any other improvements made to the plant or planned to be made and a summary of the resulting environmental benefits.
Early stages of exploring/feasibility of Carbon Capture

## Public Liasion
Annual Performance Report 2022 |  | Severn Waste Services Limited
Details of Public & Stakeholder Liaison
Summary of events held during the reporting year.
Date | Description
2022-04-22 | Community Liaison Group
List of events planned for next year
Date | Description
2022-04-24 | Community Liaison Group
2023 | Site tours to re-start for public and organized groups after 2022 affected by covid
If you wish to be involved in the public liaison programme, please contact your local Parish Councillor

## CO2 N2O
Annual Performance Report 2022 |  | Severn Waste Services Limited
Carbon dioxide emissions and biogenic content of waste inputs |  |  | Notes:
Carbon dioxide emissions (all types of plant)
Annual mass of carbon dioxide released | x tonnes | 117240
Annual mass of carbon dioxide released per tonne of waste burned | x tonnes | 0.55154
Annual mass of carbon dioxide released per MWh of energy exported | x tonnes | 0.87981
Description of how annual carbon dioxide mass emission has been calculated | Annual stack flow (kNm3) = operational hours x average hourly flow. CO2 volume = Average CO2 % x annual flow. CO2 mass = volume x density (1.26kg/Nm3) |  | Note 1: Where available, data from CO2 CEMS should be used. Otherwise, where no CEMS data is available, a suitable emissions factor should be used based on the tonnage of waste burned e.g.0.992 tCO2/t waste as per Tolvik report 2021, or other justified emissions factor - refer to embedded Environment Agency guidance note above or updated version for suitable descriptive text.
Nitrous oxide emissions (only plants which use ammonia or urea to abate NOx emissions)
Annual mass emissions of nitrous oxide | x tonnes | 17.3
Description of how annual nitrous oxide mass emission has been calculated | Annual stack flow (m3) X N2O average concentration (m3) |  | Note 2: Where available, data from N2O CEMS should be used, or if no CEMS data is available, from periodic monitoring. Otherwise, a suitable emissions factor should be used based on the tonnage of waste burned e.g. 0.0981 kgN20/t waste as per 2021 Pollution Inventory data for plants with urea-based SNCR - refer to embedded Environment Agency guidance note above or updated version for suitable descriptive text.
Total annual carbon dioxide and nitrous oxide emissions as carbon dioxide equivalent (whereby 1 t nitrous oxide is equivalent to 298 t carbon dioxide) | x tonnes CO2e | 122395
Biogenic fraction of the waste and biogenic CO2 emissions (only plants burning residual municipal waste, refuse derived fuel or solid recovered fuel)
Yearly average biogenic percentage of the waste by net calorific value (NCV) | x % | 70.8
Description of how biogenic NCV percentage has been calculated or estimated | Quarterly waste analysis is carried out by an external contractor. Data for % by CV of biogenic fractions, and total CV, has been used to attain an annual average. |  | Note 3: Where available, data from waste sampling should be used; otherwise, an estimated figure with justification can be used, or a figure assumed on the basis of a national average e.g. 2017 WRAP data for residual waste of 51.8% biogenic energy content - refer to embedded Environment Agency guidance note above or updated version for suitable descriptive text, quoting standards where relevant.
Percentage of total carbon dioxide emissions arising from biogenic waste | x % | 70.8
Description of how percentage biogenic carbon dioxide emissions have been calculated | Biogenic fraction by net calorific value assumed to be the same as the biogenic CO2 fraction of the total CO2 emissions from the plant. |  | Note 4: Examples include direct measurement via C14 method or BIOMA software - refer to embedded Environment Agency guidance note above or updated version for suitable descriptive text, quoting standards where relevant. Otherwise, as an approximation (and in lieu of any more accurate metrics which may be developed in future), the measured or estimated biogenic fraction by net calorific value can be assumed to be the same as the biogenic CO2 fraction of the total CO2 emissions from the plant.
Comments:

## Residue Quality
Annual Performance Report 2022 |  |  | Severn Waste Services Limited
Residue Quality Monitoring Requirements
Summary of monitoring undertaken and compliance
The sampling and analysis of IBA and APCr has been completed and reported at the required frequency. There were 24 IBA samples sumbitted for analysis and 4 APCr samples during the year. The laboratory results are reviewed and discussed during management meetings on a monthly basis. The results have shown that our IBA is consistant in composition and all samples submitted were found to be non-hazardous. The APCr results also demonstrate consistancy and the perameters analysed are at levels which would be condidered typical for EfW.
Commentary on any specific events
Date & Event | Description
None
Residue Quality Monitoring Results
Parameter (unit) | Limit | Normal Operation
|  | Bottom ash |  | APC Residues
Loss on Ignition (average %) | <5% | 2.4
Total Organic Carbon (average %) | <3% | 1
No. of Assessments Undertaken | --- | 24 |  | 4
No. of Hazardous Results | --- | 0
Comments :

## Water
Annual Performance Report 2022 |  |  | Severn Waste Services Limited
Emissions to Water
Summary of monitoring undertaken and compliance
There are no emissions to water.
Commentary on any specific events
Date & Event | Description
Emissions to Water / Sewer
Parameter |  | Monitoring Frequency |  | Limit | Target | Max. | Average

## Air (periodic)
Annual Performance Report 2022 |  |  | Severn Waste Services Limited
Emissions to Air (periodically monitored)
Summary of monitoring undertaken, standards used and compliance | [8 empty] | Notes:
Template may require adjustment for any bespoke monitoring requirements of permit.
Results of emissions to air that are periodically monitored
Substance | Ref. Period | Emission Limit Value |  | Average |  |  |  |  | User to add additional tables as necessary, depending on whether quarterly or bi-annual reporting is required for the compliance year
|  |  |  | A1 | A2 | A3 | A4 | A5
Hydrogen fluoride | 1 hr | 2 mg/m3 |  | 0.345
Cd and Th and their compounds | 6-8hrs | 0.05 mg/m3 |  | 0.001
Hg and its compounds | 6-8hrs | 0.05 mg/m3 |  | 0.034
Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V and their compounds | 6-8hrs | 0.5 mg/m3 |  | 0.014
Dioxins & Furans (I-TEQ) | 6-8hrs | 0.1 ng/m3 |  | 0.044
PCBs (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.009
PCBs (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.0004
PCBs (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.012
Dioxins & Furans (WHO-TEQ Humans / Mammals) | 6-8hrs | None set ng/m3 |  | 0.047
Dioxins & Furans (WHO-TEQ Fish) | 6-8hrs | None set ng/m3 |  | 0.065
Dioxins & Furans (WHO-TEQ Birds) | 6-8hrs | None set ng/m3 |  | 0.079
Anthanthrene | 6-8hrs | None set µg/m3 |  | 0.003
Benzo(a)anthracene | 6-8hrs | None set µg/m3 |  | 0.011
Benzo(a)pyrene | 6-8hrs | None set µg/m3 |  | 0.002
Benzo(b)fluoranthene | 6-8hrs | None set µg/m3 |  | 0.026
Benzo(b)naptho(2,1-d) thiophene | 6-8hrs | None set µg/m3 |  | 0.002
Benzo(c)phenanthrene | 6-8hrs | None set µg/m3 |  | 0.007
Benzo(ghi)perylene | 6-8hrs | None set µg/m3 |  | 0.009
Benzo(k)fluoranthene | 6-8hrs | None set µg/m3 |  | 0.007
Cholanthrene | 6-8hrs | None set µg/m3 |  | 0.002
Chrysene | 6-8hrs | None set µg/m3 |  | 0.031
Cyclopenta(cd)pyrene | 6-8hrs | None set µg/m3 |  | 0.0016
Dibenzo(ai)pyrene | 6-8hrs | None set µg/m3 |  | 0.0016
Dibenzo(ah)anthracene | 6-8hrs | None set µg/m3 |  | 0.0016
Fluoranthene | 6-8hrs | None set µg/m3 |  | 0.069
Indeno(123-cd) pyrene | 6-8hrs | None set µg/m3 |  | 0.001
Naphthalene | 6-8hrs | None set µg/m3 |  | 0.133
Comments :

## Air (CEMS)
Annual Performance Report 2022 | [7 empty] | Severn Waste Services Limited
Emissions to Air (continously monitored)
Notes:
Summary of monitoring undertaken, standards used and compliance | [12 empty] | Template may require adjustment for any bespoke monitoring requirements of permit
CEMs monitoring is carried out following the quality assurance procedures as stated in BS EN 14181. | [12 empty] | Report to 2 decimal places, i.e. xx.xx%
Results of emissions to air that are continuously monitored (maximum and average values for each line)
Substance | Reference Period | Emission Limit Value | A1 |  | A2 |  | A3 |  | A4 |  | A5
|  |  | Max. | Avg. | Max. | Avg. | Max. | Avg. | Max. | Avg. | Max. | Avg.
Oxides of nitrogen | Daily mean | 200 mg/m3 | 168.19 | 138.04
| ½ hourly mean | 400 mg/m3 | 232.29 | 138.04
Particulates | Daily mean | 10 mg/m3 | 5.36 | 0.97
| ½ hourly mean | 30 mg/m3 | 11.04 | 0.97
Total Organic Carbon | Daily mean | 10 mg/m3 | 3.15 | 0.32
| ½ hourly mean | 20 mg/m3 | 11.02 | 0.32
Hydrogen chloride | Daily mean | 10 mg/m3 | 9.09 | 3.58
| ½ hourly mean | 60 mg/m3 | 16.56 | 3.58
Sulphur dioxide | Daily mean | 50 mg/m3 | 24.01 | 5.15
| ½ hourly mean | 200 mg/m3 | 115.03 | 5.15
Carbon monoxide | Daily mean | 50 mg/m3 | 41.53 | 14.06
| 95%ile 10-min avg | 150 mg/m3 * | 1437.17 | 14.06
Ammonia | Daily mean | No limit set | 2.15 | 0.3
* = delete or amend as appropriate
Comments :

## HCl
Annual Performance Report 2022 |  |  |  | Severn Waste Services Limited
Monitoring of Hydrogen Chloride emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Hydrogen Chloride emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2022 | 1/2 hourly HCl ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily HCl ELV | Monthly daily mean | Highest daily maximum | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 60 | 3 | 5 | 10 | 3 | 4 | A1 | Jan
Feb | 60 | 3 | 5 | 10 | 3 | 3 |  | Feb
Mar | 60 | 3 | 8 | 10 | 3 | 4 |  | Mar |  |  |  |  | Whole Installation table A5:G18:
Apr | 60 | 3 | 7 | 10 | 3 | 4 |  | Apr |  |  |  |  | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 60 | 3 | 7 | 10 | 3 | 5 |  | May
Jun | 60 | 2 | 9 | 10 | 2 | 3 |  | Jun
Jul | 60 | 3 | 9 | 10 | 3 | 4 |  | Jul |  |  |  |  | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 60 | 2 | 7 | 10 | 2 | 3 |  | Aug
Sep | 60 | 1 | 3 | 10 | 1 | 2 |  | Sep
Oct | 60 | 7 | 13 | 10 | 7 | 9 |  | Oct
Nov | 60 | 8 | 17 | 10 | 8 | 9 |  | Nov
Dec | 60 | 5 | 14 | 10 | 5 | 9 |  | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## SO2
Annual Performance Report 2022 |  |  |  | Severn Waste Services Limited
Monitoring of Sulphur dioxide emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Sulphur dioxide emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2022 | 1/2 hourly SO2 ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily SO2 ELV | Monthly daily mean | Highest daily maximum | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 200 | 5 | 36 | 50 | 4.58 | 6 | A1 | Jan
Feb | 200 | 4 | 30 | 50 | 4.17 | 5 |  | Feb
Mar | 200 | 6 | 97 | 50 | 5.69 | 18 |  | Mar |  |  |  |  | Whole Installation table A5:G18:
Apr | 200 | 5 | 47 | 50 | 4.58 | 11 |  | Apr |  |  |  |  | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 200 | 5 | 44 | 50 | 5.29 | 24 |  | May
Jun | 200 | 6 | 115 | 50 | 6.08 | 9 |  | Jun
Jul | 200 | 6 | 44 | 50 | 5.51 | 12 |  | Jul |  |  |  |  | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 200 | 4 | 31 | 50 | 3.67 | 6 |  | Aug
Sep | 200 | 4 | 16 | 50 | 4.42 | 6 |  | Sep
Oct | 200 | 5 | 50 | 50 | 4.95 | 9 |  | Oct
Nov | 200 | 6 | 40 | 50 | 6.05 | 9 |  | Nov
Dec | 200 | 7 | 45 | 50 | 6.74 | 12 |  | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## NOx
Annual Performance Report 2022 |  |  |  | Severn Waste Services Limited
Monitoring of Oxides of Nitrogen emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Oxides of Nitrogen emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2022 | 1/2 hourly NOx ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily NOx ELV | Monthly daily mean | Highest daily maximum | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 400 | 143 | 194 | 200 | 143.4506 | 160 | A1 | Jan
Feb | 400 | 142 | 232 | 200 | 141.9257 | 160 |  | Feb
Mar | 400 | 133 | 175 | 200 | 132.9348 | 144 |  | Mar |  |  |  |  | Whole Installation table A5:G18:
Apr | 400 | 130 | 194 | 200 | 130.1547 | 140 |  | Apr |  |  |  |  | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 400 | 127 | 182 | 200 | 129.8623 | 146 |  | May
Jun | 400 | 131 | 168 | 200 | 131.302 | 140 |  | Jun
Jul | 400 | 136 | 189 | 200 | 135.7237 | 150 |  | Jul |  |  |  |  | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 400 | 139 | 180 | 200 | 138.59 | 150 |  | Aug
Sep | 400 | 131 | 182 | 200 | 134.095 | 150 |  | Sep
Oct | 400 | 198 | 150 | 200 | 150.4371 | 168 |  | Oct
Nov | 400 | 146 | 202 | 200 | 145.661 | 160 |  | Nov
Dec | 400 | 142 | 190 | 200 | 142.381 | 160 |  | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## TOC
Annual Performance Report 2022 |  |  |  | Severn Waste Services Limited
Monitoring of Total organic carbon emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Total organic carbon emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2022 | 1/2 hourly TOC ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily TOC ELV | Monthly daily mean | Highest daily maximum | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 20 | 0 | 6 | 10 | 0.022581 | 0 | A1 | Jan
Feb | 20 | 0 | 4 | 10 | 0.032857 | 0 |  | Feb
Mar | 20 | 0 | 6 | 10 | 0.062258 | 0 |  | Mar |  |  |  |  | Whole Installation table A5:G18:
Apr | 20 | 0 | 7 | 10 | 0.094 | 0 |  | Apr |  |  |  |  | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 20 | 0 | 10 | 10 | 0.10839 | 0 |  | May
Jun | 20 | 0 | 6 | 10 | 0.149 | 0 |  | Jun
Jul | 20 | 0 | 11 | 10 | 0.13613 | 0 |  | Jul |  |  |  |  | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 20 | 0 | 8 | 10 | 0.454 | 1 |  | Aug
Sep | 20 | 1 | 4 | 10 | 1.011 | 2 |  | Sep
Oct | 20 | 1 | 10 | 10 | 0.80742 | 1 |  | Oct
Nov | 20 | 1 | 11 | 10 | 0.508 | 1 |  | Nov
Dec | 20 | 0 | 8 | 10 | 0.47355 | 1 |  | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## Particulates
Annual Performance Report 2022 |  |  |  | Severn Waste Services Limited
Monitoring of Particulate matter emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Particulate matter emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2022 | 1/2 hourly PM ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily PM ELV | Monthly daily mean | Highest daily maximum | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 30 | 2 | 11 | 10 | 2.1181 | 3 | A1 | Jan
Feb | 30 | 1 | 3 | 10 | 1.3343 | 2 |  | Feb
Mar | 30 | 1 | 3 | 10 | 1.0094 | 1 |  | Mar |  |  |  |  | Whole Installation table A5:G18:
Apr | 30 | 1 | 2 | 10 | 0.95115 | 1 |  | Apr |  |  |  |  | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 30 | 1 | 3 | 10 | 0.84903 | 1 |  | May
Jun | 30 | 1 | 1 | 10 | 0.84667 | 1 |  | Jun
Jul | 30 | 1 | 3 | 10 | 0.90935 | 1 |  | Jul |  |  |  |  | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 30 | 1 | 2 | 10 | 1.0675 | 1 |  | Aug
Sep | 30 | 1 | 11 | 10 | 0.627 | 2 |  | Sep
Oct | 30 | 0 | 1 | 10 | 0.49 | 1 |  | Oct
Nov | 30 | 1 | 1 | 10 | 0.75033 | 1 |  | Nov
Dec | 30 | 1 | 1 | 10 | 0.69097 | 1 |  | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0

## CO 95% 10 min
Annual Performance Report 2022 |  |  |  | Severn Waste Services Limited
Monitoring of Carbon Monoxide (10-minute avg) |  |  |  | Whole Installation |  |  | See Notes in Cell S3 | Monitoring of Carbon Monoxide (10-minute avg) |  |  |  |  | Per Combustion Line |  | Notes: | Notes:
User to add logic to complete Whole installation, Table A5:H18. From the data in Per Combustion Line, Table K6:Q79, subject to No. of lines installed
mg/Nm3 | 10-minute Reference Periods |  |  |  | Daily Reference Periods
2022 | 95%ile 10-min avg CO ELV | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Daily CO ELV | Monthly daily mean | Highest daily maximum |  | 2022 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
Jan | 150 | 27 | 12 | 460 | 50 | 11.9 | 15 |  | A1 | Jan
Feb | 150 | 79 | 14 | 470 | 50 | 13.83 | 20 |  |  | Feb
Mar | 150 | 56 | 15 | 579 | 50 | 14.5387 | 21 |  |  | Mar | [5 empty] | Whole Installation table A5:H18:
Apr | 150 | 75 | 16 | 876 | 50 | 16.3523 | 23 |  |  | Apr | [5 empty] | Mean: for 10-min and daily periods use average of all operational combustion lines.
May | 150 | 111 | 18 | 744 | 50 | 18.2948 | 29 |  |  | May
Jun | 150 | 110 | 19 | 734 | 50 | 18.7617 | 26 |  |  | Jun
Jul | 150 | 172 | 20 | 1239 | 50 | 19.6742 | 42 |  |  | Jul | [5 empty] | Maximum: for 10-min and daily periods use the highest of all operational combustion lines in any month.
Aug | 150 | 113 | 22 | 1381 | 50 | 21.713 | 41 |  |  | Aug
Sep | 150 | 14 | 5 | 254 | 50 | 5.466 | 7 |  |  | Sep
Oct | 150 | 29 | 6 | 749 | 50 | 6.3377 | 12 |  |  | Oct
Nov | 150 | 54 | 11 | 1437 | 50 | 11.359 | 21 |  |  | Nov
Dec | 150 | 39 | 10 | 1221 | 50 | 10.4332 | 20 |  |  | Dec
[10 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0
[9 empty] | 2022 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[10 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0
[9 empty] | 2022 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [9 empty] | Dec
Environment Agency explanatory note: The 10-minute average ELV is based on the “95th percentile”. In this case this means that 95% of the 10 minute averages in the relevant 24-hour period (i.e. 137) must be below 150 mg/Nm3, and 5% (i.e. 7) are allowed to be any value above 150 mg/Nm3. Whilst we expect operators to minimise CO emissions at all times, it is perfectly acceptable for the value of the maximum 10-minute average to be above 150 mg/Nm3, provided the 95th percentile ELV has been met for that period. | [9 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0
[9 empty] | 2022 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[10 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0
[9 empty] | 2022 | mg/Nm3 | 95%ile 10-min avg maximum | Monthly CO 10-min avg mean | 10-min avg maximum | Monthly daily mean | Monthly daily maximum
[9 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[10 empty] | Annual | #DIV/0! |  | 0 | #DIV/0! | 0

## NH3
Annual Performance Report 2022 |  |  |  | Severn Waste Services Limited
Monitoring of Ammnonia emissions |  |  | Whole Installation |  |  | See Notes in Cell Q3 | Monitoring of Ammnonia emissions |  |  |  | Per Combustion Line |  | Notes:
User to add logic to complete Whole installation, Table A5:G18. From the data in Per Combustion Line, Table J6:O79, subject to No. of lines installed
mg/Nm3 | 1/2 Hourly Reference Periods |  |  | Daily Reference Periods
2022 | 1/2 hourly NH3 ELV | Monthly 1/2 hourly mean | Highest 1/2 hourly maximum | Daily NH3 ELV | Monthly daily mean | Highest daily maximum | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
Jan | 0 | 0 | 1 | 10 | 0.017419 | 0 | A1 | Jan
Feb | 0 | 0 | 0 | 10 | 0.0082143 | 0 |  | Feb
Mar | 0 | 0 | 1 | 10 | 0.016774 | 0 |  | Mar |  |  |  |  | Whole Installation table A5:G18:
Apr | 0 | 0 | 0 | 10 | 0.02 | 0 |  | Apr |  |  |  |  | Mean: for 1/2 hourly and daily periods calculate mean of values across all operational combustion lines for the month
May | 0 | 0 | 1 | 10 | 0.0070968 | 0 |  | May
Jun | 0 | 0 | 1 | 10 | 0.011 | 0 |  | Jun
Jul | 0 | 0 | 2 | 10 | 0.029 | 0 |  | Jul |  |  |  |  | Maximum: for 1/2 hourly and daily periods use the highest value across all operational combustion lines for the month
Aug | 0 | 0 | 2 | 10 | 0.2085 | 1 |  | Aug
Sep | 0 | 1 | 16 | 10 | 1.029 | 2 |  | Sep
Oct | 0 | 1 | 2 | 10 | 0.69226 | 1 |  | Oct
Nov | 0 | 1 | 2 | 10 | 0.76733 | 1 |  | Nov
Dec | 0 | 1 | 1 | 10 | 0.81226 | 1 |  | Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A2 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A3 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Comments : | [7 empty] | Dec
An indicated ELV value of zero in the table above means that no ammonia limit is set in the permit. | [7 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A4 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0
[7 empty] | 2022 | mg/Nm3 | Monthly 1/2 hourly mean | Monthly 1/2 hourly maximum | Monthly daily mean | Monthly daily maximum
[7 empty] | A5 | Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
[8 empty] | Annual | #DIV/0! | 0 | #DIV/0! | 0